## modbus format
Data format: 9600 8-bit data, 1 stop bit, no checksum
Support modbus protocol 3 6 16. The data format is high bit first, low bit last.
Message protocol format: read register, request frame
BYTE | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Field definition | ADDR | CMD | MSB | LSB | MSB | LSB | CRC-L | CRC-H
describe | 0x81 | 0x03 | Register starting address |  | Number of registers N |  | CRC-16 check
Description: 81-03-00-00-00-7F-1B-EA 81 is the slave address, 03 is the read command, 0000 is the register starting address, 007F means the number of read registers is 127, which is the read command. 1BEA is the CRC check code.
Regular response frame
BYTE | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Field definition | ADDR | CMD | Length | MSB | LSB | MSB | LSB | CRC-L | CRC-H
describe | 0x51 | 0x03 | Data length L=2*N | The value of the first register |  | ...the value of the Nth register |  | CRC-16 check
Note: N is the register data 51 03 FE xx xx... 51 is the slave address, 03 is the read command, FE is the length of the read data,
Message protocol format: write register, request frame
BYTE | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Field definition | ADDR | CMD | MSB | LSB | MSB | LSB | CRC-L | CRC-H
describe | 0x81 | 0x06 | Register address |  | data |  | CRC-16 check
Description: 81-06-01-16-03-E8-76-8C D2 is the slave address, 06 is the instruction to write a single holding register, 000C is the register address, 0001 indicates the host command to discharge the battery, and 9BAA is the CRC check code.
Regular response frame
BYTE | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Field definition | ADDR | CMD | MSB | LSB | MSB | LSB | CRC-L | CRC-H
describe | 0x51 | 0x06 | Register address |  | data |  | CRC-16 check
Description: 51-06-01-16-03-E8-65-1C Write a single holding register The regular response frame has the same format as the request frame.
Message protocol format: write multiple data registers, request frame
BYTE | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Field definition | ADDR | CMD | MSB | LSB | MSB | LSB | MSB | LSB | CRC-L | CRC-H
describe | 0x81 | 0x10 | Register starting address |  | Register length(N) |  | Data content(2N) |  | CRC-16 check
Description: 81-10-01-0B-00-02-00-01-86-A0-DA-FE 0x81 is the slave address, 0x10 means writing multiple data register instructions, 0x01B0 is the register starting address, 0x0002 means continuous Write two registers, 0x0001 represents the data written in the first register, 0x86A0 represents the data written in the second register, and 0xDAFE represents the CRC16 check code.
Regular response frame
BYTE | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Field definition | ADDR | CMD | MSB | LSB | MSB | LSB | CRC-L | CRC-H
describe | 0x51 | 0x10 | Register starting address |  | Register length(N) |  | CRC-16 check
Description: 51-10-01-0B-00-02-3D-A6 0x51 is the slave address, 0x10 is the instruction to write multiple data registers, 0x010B is the register starting address, 0x0002 means writing two registers continuously, 0x3DA6 means CRC16 Check code.

## Real-time data
Protection board protocol description
Data format: 9600 8-bit data, 1 stop bit, no checksum
Support modbus protocol 3 6 16 | The data format is high bit first, low bit last
address | type of data | Read and write | content | scope | Data calculation instructions
0x00~0x2F | unsigned short int | R | Single battery voltage, every two bytes is a battery voltage | 0--5000 | 0.001 3550*0.001=3.550v
0x30~0x37 |  | R | battery temperature | 0--140 (-40 to 100℃) | The temperature data is offset by 40. For example, when the temperature data is 40, the actual temperature = temperature data-40;
0x38 |  | R | total battery voltage |  | 0.1V 350*0.1=35.0v
0x39 |  | R | Current data | 0--65535 | 0.1A, 30000 Offset, the charging current is a negative number, and the discharge is a positive number, (30080-30000)*0.1=8A, which is the discharge current
0x3A |  | R | SOC | 0--65535 | 0.001,800/1000=80%
0x3B |  | R | LIFE | 0--65535 | Heartbeat bag
0x3C |  | R | Battery quantity
0x3D |  | R | Battery temperature sensor quantity
0x3E |  | R | Maximum cell voltage | 0--65535 | 1mv
0x3F |  | R | Highest cell voltage serial number | 0--65535 | 1
0x40 |  | R | Minimum cell voltage | 0--65535 | 1mv
0x41 |  | R | Minimum cell voltage serial number | 0--65535 | 1
0x42 |  | R | Maximum and minimum cell voltage difference | 0--65535 | 1mv
0x43 |  | R | Maximum cell temperature | 0--65535 | 1°C, the temperature data is offset by 40. For example, when the temperature data is 40, the actual temperature = temperature data-40;
0x44 |  | R | Maximum unit temperature serial number | 0--65535 | 1
0x45 |  | R | Minimum cell temperature | 0--65535 | 1°C, the temperature data is offset by 40. For example, when the temperature data is 40, the actual temperature = temperature data-40;
0x46 |  | R | Minimum cell temperature serial number | 0--65535 | 1
0x47 |  | R | Maximum and minimum unit temperature temperature difference | 0--65535 | 1°C
0x48 |  | R | Charge and discharge status | 0--65535 | 0 stationary, 1 charging, 2 discharging
0x49 |  | R | Charger status | 0--65535 | 0: Unable to detect charger 1: Charger detected
0x4A |  | R | Load status | 0--65535 | 0: Unable to detect load 1: Load detected
0x4B |  | R | Battery remaining capacity |  | 0.1AH
0x4C |  | R | Battery cycle times
0x4D |  | R | equilibrium state | 0--65535 | 0: Off 1: Passive balancing 2: Active balancing
0x4E |  | R | Balanced current | 0--65536 | 0.1A
0x4F~0x51 |  | R | equilibrium position | 0--65536 | Each bit represents a battery
0x52 |  | R | Charging MOS status | 0--65535 | 0: off 1: on
0x53 |  | R | Discharge MOS status | 0--65535 | 0: off 1: on
0x54 |  | R | Precharge MOS status | 0--65535 | 0: off 1: on
0x55 |  | R | Heating MOS status | 0--65535 | 0: off 1: on
0x56 |  | R | Fan MOS status | 0--65535 | 0: off 1: on
0x57 |  | R | average voltage | 0--65535 | 1mV
0x58 |  | R | power | 0--65535 | W
0x59 |  | R | energy | 0--65535 | 1WH
0x5A |  | R | MOS temperature | 0--65535 | 1°C, the temperature data is offset by 40. For example, when the temperature data is 40, the actual temperature = temperature data-40;
0x5B |  | R | ambient temperature | 0--65535 | 1°C, the temperature data is offset by 40. For example, when the temperature data is 40, the actual temperature = temperature data-40;
0x5C |  | R | Heating temperature | 0--65535 | 1°C, the temperature data is offset by 40. For example, when the temperature data is 40, the actual temperature = temperature data-40;
0x5D |  | R | Heating current | 0--65535 | 1A/bit
0x5E |  | R | Remaining mileage | 0--65536 | 0.1km
0x5F |  | R | Current limiting state | 0--65536 | 1 turns on current limiting 0 turns off current limiting
0x60 |  | R | current limit | 0--65536 | 0.1A/bit offset -30000, less than 30000 is negative, greater than 30000 is positive
0x61~0x63 |  | R | RTC | 0--65536 | Year, month, day/hour, minute and second, for example, 08:30:56 on August 15, 2020, then send 0x14080F081E38
0x64 |  | R | Remaining charging time | 0--65536 | min
0x65 |  | R | DI/DO status | 0--65535 | Low byte bit0: DI1 (0:OFF 1:ON) bit1: DI2 (0:OFF 1:ON) bit2: DI3 (0:OFF 1:ON) bit3: DI4 (0:OFF 1:ON) bit4: DI5 (0:OFF 1:ON) bit5: DI6 (0:OFF 1:ON) bit6: DI7 (0:OFF 1:ON) bit7: DI8 (0:OFF 1:ON) High byte bit8: DO1 (0: OFF 1:ON) bit9:DO2 (0:OFF 1:ON) bit10:DO3 (0:OFF 1:ON) bit11:DO4 (0:OFF 1:ON) bit12:DO5 (0:OFF 1:ON) bit13 :DO6（0:OFF 1:ON） bit14:DO7（0:OFF 1:ON） bit15:DO8（0:OFF 1:ON）
0x66 |  | R | Fault status 1 | 0--65535 | Byte 0 Bit 0: Level 1 alarm when the cell voltage is too high Bit 1: Level 2 alarm when the cell voltage is too high Bit 2: Level 1 alarm when the cell voltage is too low Bit 3: Level 2 alarm when the cell voltage is too low Bit 4: Total voltage Too high first level alarm Bit 5: The total voltage is too high and the second level alarm Bit 6: The total voltage is too low and the first level alarm Bit 7: The total voltage is too low and the second level alarm Byte 1 Bit 0: The charging temperature is too high and the first level alarm Bit 1: Charging Temperature is too high. Level 2 alarm Bit 2: Charging temperature is too low. Level 1 alarm Bit 3: Charging temperature is too low. Level 2 alarm Bit 4: Discharge temperature is too high. Level 1 alarm Bit 5: Discharge temperature is too high. Level 2 alarm Bit 6: Discharge temperature is too high. Lower level alarm Bit 7: Discharge temperature is too low Level 2 alarm
0x67 |  | R | Fault status 2 | 0--65535 | Byte 0 Bit 0: Charging overcurrent level 1 alarm Bit 1: Charging overcurrent level 2 alarm Bit 2: Discharge overcurrent level 1 alarm Bit 3: Discharge overcurrent level 2 alarm Bit 4: SOC is too high level 1 alarm Bit 5: SOC is too high, Level 2 alarm Bit 6: SOC is too low, Level 1 alarm Bit 7: SOC is too low, Level 2 alarm Byte 1 Bit 0: Level 1 alarm when the pressure difference is too large Bit 1: Level 2 alarm when the pressure difference is too large Bit 2: Level 1 alarm when the temperature difference is too large Bit 3: Level 2 alarm when the temperature difference is too large Bit 4: Level 1 alarm when the mos temperature is too high Bit 5: Mos temperature is too high, level 2 Bit 6: ambient temperature is too high, level 1 Bit 7: ambient temperature is too high, level 2
0x68 |  | R | Fault status 3 | 0--65535 | Byte 0 Bit 0: Charging MOS over-temperature warning Bit 1: Discharging MOS over-temperature warning Bit 2: Charging MOS temperature detection sensor failure Bit 3: Discharging MOS temperature detection sensor failure Bit 4: Charging MOS adhesion failure Bit 5: Discharge MOS adhesion failure Bit 6: Charging MOS open circuit fault Bit 7: Discharging MOS open circuit fault Byte 1 Bit 0: AFE acquisition chip fault Bit 1: Single unit acquisition offline Bit 2: Single unit temperature sensor fault Bit 3: EEPROM storage fault Bit 4: RTC clock Fault Bit 5: Precharge failure Bit 6: Vehicle communication failure Bit 7: Intranet communication module failure
0x69 |  | R | Fault status 4 | 0--65535 | Byte 0: Bit 0: Current module fault Bit 1: Internal total voltage detection module fault Bit 2: Short circuit protection fault Bit 3: Low voltage charging prohibition fault Bit 4: GPS or soft switch disconnects MOS Bit 5: Charging cabinet is offline Bit6~Bit7 : Reserved
0x6A |  | R | Backup acquisition current | 0--65536 | 0.1A, 30000 Offset, the charging current is a negative number, and the discharge is a positive number, (30080-30000)*0.1=8A, which is the discharge current
0x6B |  | R | Wake-up source | 0--65536 | bit0: key bit1: button bit2: 485 bit3: can bit4: current
0x6C |  | R | xxx | 0--65536 | reserved
0x6D |  | R | New fault code 0-1 | 0--65536 | Low byte: bit2:0, single overvoltage alarm level bit5:3, single undervoltage alarm level bit6, smart charger connection bit7, smart charger connection failure high byte bit2:0, excessive voltage difference alarm level bit5:3, charging high temperature alarm level bit6, smart discharge device connection bit7, smart discharge device connection failed
0x6E |  | R | New fault code 2-3 | 0--65536 | Low byte bit2:0, charging low temperature alarm level bit5:3, discharge high temperature alarm level bit6, charging MOS temperature is too high bit7, charging MOS temperature detection fault high byte bit2:0, discharge low temperature alarm level bit5:3, temperature difference is too high Big alarm level bit6, discharge MOS temperature is too high, bit7, discharge MOS temperature detection failure
0x6F |  | R | New fault code 4-5 | 0--65536 | Low byte bit2:0, total voltage too high alarm level bit5:3, total voltage too low alarm level bit6, short circuit protection bit7, reserved high byte bit2:0, charging overcurrent alarm level bit5:3, discharge overcurrent Alarm level bit6, low voltage prohibits charging bit7 high voltage prohibits discharge
0x70 |  | R | New fault code 6-7 | 0--65536 | Low byte bit2:0, soc too low alarm level bit5:3, soh too low alarm level bit6, parallel communication successful bit7, parallel communication failed high byte bit2:0, MOS temperature too high alarm level bit5:3, thermal runaway Alarm level bit6, reserved bit7, reserved
0x71 |  | R | New fault code 8-9 | 0--65536 | Low byte bit2:0, reserved bit5:3, reserved bit6, reserved bit7, reserved high byte bit2:0, reserved bit5:3, reserved bit6, reserved bit7, reserved
0x72 |  | R | New fault code 10-11 | 0--65536 | Low byte bit2:0, reserved bit5:3, reserved bit6, reserved bit7, reserved high byte bit0, afe chip fault bit1, afe communication fault bit2, afe sampling fault bit3, voltage detection fault bit4, voltage acquisition Line disconnection bit5, total voltage detection fault bit6, current detection fault bit7, temperature detection fault
0x73 |  | R | New fault code 12-13 | 0--65536 | Low byte bit, 0, temperature acquisition line disconnected bit1, eeprom fault bit2, flash fault bit3, rtc fault bit4, charging mos fault bit5, discharging mos fault bit6, precharge mos fault bit7, precharge failure high byte bit0, The communication command controls charging mos off bit1, the communication command controls discharging mos off bit2, the switch controls charging mos off bit3, the switch controls charging mos off bit4, the fan works bit5, the heating works bit6, the current limiting module works
0x74 |  | R | Sample current | 0--65536 | offset 30000;0.1
0x75 |  | R | Sampling current coefficient | 0--65536 | 0.0001
0x76 |  | R | Sample current offset | 0--65536 | 0.1
0x77 |  | R | Sampling current Ad | 0--65536
0x78 |  | R | PWM1_Duty | 0--65536 | 0.1%
0x79 |  | R | Reserved signal 16 | 0--65536
0x7a |  | R | Reserved signal 17 | 0--65536
0x7b |  | R | Reserved signal 18 | 0--65536
0x7c |  | R | Reserved signal 19 | 0--65536
0x7d |  | R | Reserved signal 20 | 0--65536
0x7e